## Table 1
TAG NUMBER | QTY OF ITEMS | DESCRIPTION | SIZE |  | VOLTS | PHASE | FREQUENCY | SHIPPING WEIGHT | SHIPPING DIMENSIONS | MFR | MODEL | SUPPLIED BY (COMPANY, CONTRACTOR, FABRICATOR) | PO AND PO LINE NO. (IF COMPANY SUPPLY) | COMMENTS | REV
[7 empty] | Hz | kg | m
KXL-EES-01 | [13 empty] | All Sites
XXX-AAAAA-B0-EES-01 | 1 | Electrical Equipment Shelter - Premanufactured Steel building | 18593 x 4267 x 3962 |  |  |  |  | 38555 |  | Koontz Wagner
KXL-VES-01 | [13 empty] | All Sites
XXX-AAAAA-B0-VES-01 | 1 | VFD Equipment Shelter - Premanufactured Steel building | 10668 x 4267 x 4318 |  |  |  |  | 39689 |  | Koontz Wagner
KXL-MV-VFD
XXX-AAAAA-B0-VFD-01 | 1 | MV 6500hp VFD | 7823 x 1372 x 3256 |  | 6.9kV | 3 | 60 | - |  | Siemens
XXX-AAAAA-B0-LBS-01 | 1 | MV VFD Incomer Load Break Switch | 914 x 1118 x 2362 |  | 6.9kV | 3 | 60 | - |  | Siemens
XXX-AAAAA-B0-ACP-03 | 1 | 480V Auxiliary Distribution Panel |  |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-LDP-01 | 1 | Lighting Distribution Panel |  |  | 120/ 240V | 1 | 60 |  |  | Siemens
XXX-AAAAA-B0-TL-01 | 1 | Lighting Distribution Transformer |  |  | 480- 240/120V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-HVAC-04 | 1 | Panel HVAC Unit 4, 30 Ton |  |  | 480V | 3 | 60 |  |  | Specific Systems
XXX-AAAAA-B0-HVAC-05 | 1 | Panel HVAC Unit 5, 30 Ton |  |  | 480V | 3 | 60 |  |  | Specific Systems
XXX-AAAAA-B0-HVAC-06 | 1 | Panel HVAC Unit 6, 30 Ton |  |  | 480V | 3 | 60 |  |  | Specific Systems
XXX-AAAAA-B0-EJB-1011 | 1 | Control Interface Panel
PUMP STATION - ELECTRIC EQUIPMENT OUTDOOR | [13 empty] | All Sites
XXX-AAAAA-B0-DT-01 | 1 | Station Service Transformer 600kVA, 6900-480V | 2753 x 1878 x 1907 | 6900-480V |  | 3 | 60 | 3719 |  | Virginia Transformer
XXX-AAAAA-B0-EG-01 | 1 | Emergency Genarator | 4826 x 1013 x 3070 | 480V |  | 3 | 60 | 3960 |  | Generac
XXX-AAAAA-B0-GCP-01 | 1 | Emergency Genarator control panel |  | 208V |  | 3 | 60 |  |  | Generac
PUMP STATION - ELECTRIC MOTORS
MAINLINE PUMP MOTORS - 6.6kV
XXX-AAAAA-B1-MPM-01 | 1 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV |  | 3 | 60 | 11440 |  | Siemens
XXX-AAAAA-B2-MPM-02 | 1 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV |  | 3 | 60 | 11440 |  | Siemens
XXX-AAAAA-B3-MPM-03 | 1 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV |  | 3 | 60 | 11440 |  | Siemens
XXX-AAAAA-B4-MPM-04 | 1 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV |  | 3 | 60 | 11440 |  | Siemens
MISC MOTORS - 460VAC | [13 empty] | All Sites
XXX-AAAAA-B0-PM-01 | 1 | Re-Injection Pump - 460VAC, 25 HP, 1.15 S.F, 1800RPM, TEFC, CL 1, DIV.1 GR D |  | 460V |  | 3 | 60 |  |  | WEG Industrial SA
PUMP STATION - ELECTRIC ACTUATORS
MAINLINE PUMP ACTUATORS
XXX-AAAAA-B1-MOV-1011 | 1 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B1-MOV-1012 | 1 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM |  |  |  |  | 2
XXX-AAAAA-B2-MOV-1021 | 1 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B2-MOV-1022 | 1 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM |  |  |  |  | 2
XXX-AAAAA-B3-MOV-1031 | 1 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B3-MOV-1032 | 1 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM |  |  |  |  | 2
XXX-AAAAA-B4-MOV-1041 | 1 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B4-MOV-1042 | 1 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM |  |  |  |  | 2
KXL-MV-SWGR | [13 empty] | All Sites
XXX-AAAAA-B0-SWGR-01 | 1 | 6.9kV SWGR | 2413 x 2591 x 2632 |  | 6.9kV | 3 | 60 | 3602 |  | Siemens
XXX-AAAAA-B0-B-01 | 1 | 6.9kV Bus, 3000A |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-64-T-01 | 1 | Ground Fault Relay | [7 empty] | Startco
XXX-AAAAA-B0-52-B-01 | 1 | 6.9kV Breaker, 3000A (MAIN) |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-MFR-B-01 | 1 | Multi Function Relay | [7 empty] | Siemens
XXX-AAAAA-B0-MFR-PFCB-01 | 1 | Multi Function Relay | [7 empty] | Siemens
Breaker PFC UNIT
XXX-AAAAA-B0-52-PFCB-01 | 1 | 6.9kV Breaker, 1200A (POWER FACTOR CAPACITOR UNIT) |  |  | 6.9kV | 3 | 60 |  |  | Siemens |  |  |  | See designation table for sub area code and facility names
KXL-MV-MCC | [13 empty] | All Sites except for Leigh and Burns. Burns - 3 units only
XXX-AAAAA-B0-MCC-01 | 1 | 6.9kV MCC | 4648 x 1219 x 2608 |  | 6.9kV | 3 | 60 | 3515 |  | Siemens
XXX-AAAAA-B0-B-01 | 1 | 6.9kV Bus, 3000A |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-89-VFD-01 | 1 | 6.9kV Contactor, 720A (VFD INPUT) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B0-MFR-VFD-01 | 1 | Multi Function Relay | [7 empty] | Siemens
XXX-AAAAA-B0-89-DT-01 | 1 | 6.9kV Contactor, 720A Station Service Transformer |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-MFR-DT-01 | 1 | Multi Function Relay | [7 empty] | Siemens
XXX-AAAAA-B1-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B1-MFR-MPM-01 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B2-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B2-MFR-MPM-02 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B3-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B3-MFR-MPM-03 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B4-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B4-MFR-MPM-04 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B5-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B5-MFR-MPM-05 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B0-MCC-02 | 1 | 6.9kV MCC | 3658 x 914 x 2286 |  | 6.9kV | 3 | 60 | 2812 |  | Siemens
XXX-AAAAA-B0-B-02 | 1 | 6.9kV Bus, 1200A (VFD) |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-89-VFD-02 | 1 | 6.9kV Contactor, 720A (Isolation Output VFD) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B1-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B2-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B3-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B4-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B5-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
KXL-LV-MCC | [13 empty] | All Sites
XXX-AAAAA-B0-MCC-03 | 1 | 480V MCC | 2540 x 508 x 2286 * |  | 480V | 3 | 60 |  |  | Siemens |  |  |  | Size may vary in some stations.
XXX-AAAAA-B0-B-03 | 1 | 480V Bus, 800A |  |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-52-B-02 | 1 | 480V Breaker, 800A |  |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-MFR-B-02 | 1 | Multi Function Relay | [7 empty] | Siemens
XXX-AAAAA-B0-MCC-04 | 1 | 480V MCC (Emergency MCC) | 2540 x 508 x 610 |  | 480V | 3 | 60 |  |  | Siemens |  |  |  | Size may vary in some stations.
XXX-AAAAA-B0-B-04 | 1 | 480V Bus, 800A |  |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-ATS-01 | 1 | 480V Automatic transfer switch, 260A 3PH |  |  | 480V | 3 | 60 |  |  | ASCO
MISC KXL-EES-01 EQUIP'T | [13 empty] | All Sites
XXX-AAAAA-B0-DT-02 | 1 | Auxiliary Distribution Transformer 45kVA, 480-208/120V |  |  | 480- 208/120V | 3 | 60 |  |  | Hammond
XXX-AAAAA-B0-DT-03 | 1 | Auxiliary Distribution Transformer 45kVA, 480-208/120V |  |  | 480- 208/120V | 3 | 60 |  |  | Hammond
XXX-AAAAA-B0-UPS-01 | 1 | UPS, 7.5 kVA | 762 x 914 x 2007 |  | 208V | 3 | 60 | 422 |  | Ametek
XXX-AAAAA-B0-UACP-01 | 1 | 120V UPS Distribution Panel |  |  | 120VDC |  |  |  |  | Ametek
XXX-AAAAA-B0-BB-01 | 1 | UPS Battery Bank |  |  | 125VDC |  |  |  |  | East Pen
XXX-AAAAA-B0-ACP-01 | 1 | 208/120V Power Panel |  |  | 208/120V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-ACP-02 | 1 | 208/120V Power Panel |  |  | 208/120V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-EHTC-01 | 1 | EHT Control Panel | [7 empty] | Thermon |  |  |  | Not required for Gulf Coast Sites
XXX-AAAAA-B0-UCP-01 | 1 | Unit Control Panel | [7 empty] | Siemens
XXX-AAAAA-B0-SCP-01 | 1 | Station Control Panel | [7 empty] | GE
XXX-AAAAA-B0-HVAC-01 | 1 | Panel HVAC Unit 1, 6 Ton |  |  | 480V | 3 | 60 |  |  | Bard
XXX-AAAAA-B0-HVAC-02 | 1 | Panel HVAC Unit 2, 6 Ton |  |  | 480V | 3 | 60 |  |  | Bard
XXX-AAAAA-B0-HVAC-03 | 1 | Panel HVAC Unit 3, 6 Ton |  |  | 480V | 3 | 60 |  |  | Bard
XXX-AAAAA-B0-SCMP-01 | 1 | Station Communication Panel
XXX-AAAAA-B0-CR-01 | 1 | Cathodic Protection Rectifier | [7 empty] | Corrpro |  |  |  | Site specific - if required
XXX-AAAAA-B0-SCMP-03 | 1 | Service Entrance Box | [7 empty] | Siemens
XXX-AAAAA-B0-CP-01 | 1 | Mimic Panel | [7 empty] | Koontz Wagner
Rexa Panel/ Transformer
XXX-AAAAA-B0-PFCB-01 | 1 | Power Factor Capacitor Bank |  |  | 6.9kV | 3 | 60 |  |  | Power Survey
STATION ACTUATORS
Sites with 3-valve cluster
XXX-AAAAA-B0-MOV-0101 | 1 | Suction - 460VAC, 1.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0205 | 1 | Disch. - 460VAC, 1.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0102 | 1 | Bypass - 460VAC, 1.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
Sites with trap
XXX-AAAAA-B0-MOV-0101 | 1 | Suction - 460VAC, 0.25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0205 | 1 | Discharge - 460VAC, 0.25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0102 | 1 | Bypass - 460VAC, 6.0 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
PIG TRAP ACTUATORS
XXX-AAAAA-B0-MOV-0103 | 1 | Receiver - 460VAC, 25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0104 | 1 | Receiver - 460VAC, 25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0107 | 1 | Receiver - 460VAC, 30 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0203 | 1 | Launcher - 460VAC, 25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0204 | 1 | Launcher - 460VAC, 25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0207 | 1 | Launcher - 460VAC, 30 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
EHT CONTROLLER FOR SUMP TANK
XXX-AAAAA-B0-EHTC-03 | 1 | EHT Control Panel, Part No. TCM2-1-SSR30B/1R-240-I-1SS3-H1-1-1-178525 | [7 empty] | Thermon |  | CONTRACTOR |  |  | 2

## Sheet2
stand alone equipment |  | equipment to stay in bldg
TAG NUMBER | QTY | DESCRIPTION | SIZE | VOLTS | PHASE | FREQUENCY | SHIPPING WEIGHT |  | MFR | MODEL | COMMENTS
|  |  | mm |  |  | Hz | kg | lbs (conversion cell below)
KXL-EES-01 | [7 empty] | 2.2 |  |  | All Sites
XXX-AAAAA-B0-EES-01 | 4 | Electrical Equipment Shelter - Premanufactured Steel building | 18593 x 4267 x 3962 |  |  |  | 38555 | 84821 | Koontz Wagner
KXL-VES-01 | [10 empty] | All Sites
XXX-AAAAA-B0-VES-01 | 4 | VFD Equipment Shelter - Premanufactured Steel building | 10668 x 4267 x 4318 |  |  |  | 39689 | 87315.8 | Koontz Wagner
KXL-MV-VFD
XXX-AAAAA-B0-VFD-01 | 4 | MV 6500hp VFD | 7823 x 1372 x 3256 | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-LBS-01 | 4 | MV VFD Incomer Load Break Switch | 914 x 1118 x 2362 | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-ACP-03 | 4 | 480V Auxiliary Distribution Panel |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-LDP-01 | 4 | Lighting Distribution Panel |  | 120/ 240V | 1 | 60 |  |  | Siemens
XXX-AAAAA-B0-TL-01 | 4 | Lighting Distribution Transformer |  | 480- 240/120V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-HVAC-04 | 4 | Panel HVAC Unit 4, 30 Ton |  | 480V | 3 | 60 |  |  | Specific Systems
XXX-AAAAA-B0-HVAC-05 | 4 | Panel HVAC Unit 5, 30 Ton |  | 480V | 3 | 60 |  |  | Specific Systems
XXX-AAAAA-B0-HVAC-06 | 4 | Panel HVAC Unit 6, 30 Ton |  | 480V | 3 | 60 |  |  | Specific Systems
XXX-AAAAA-B0-EJB-1011 | 4 | Control Interface Panel
PUMP STATION - ELECTRIC EQUIPMENT OUTDOOR | [10 empty] | All Sites
XXX-AAAAA-B0-DT-01 | 4 | Station Service Transformer 600kVA, 6900-480V | 2753 x 1878 x 1907 | 6900-480V | 3 | 60 | 3719 | 8181.8 | Virginia Transformer
XXX-AAAAA-B0-EG-01 | 4 | Emergency Genarator | 4826 x 1013 x 3070 | 480V | 3 | 60 | 3960 | 8712 | Generac | SD100 | Level 2 acoustic enclosure. Fuel tank larger than spec sheet max. -Will S.
XXX-AAAAA-B0-GCP-01 | 4 | Emergency Genarator control panel |  | 208V | 3 | 60 |  |  | Generac
PUMP STATION - ELECTRIC MOTORS
MAINLINE PUMP MOTORS - 6.6kV
XXX-AAAAA-B1-MPM-01 | 4 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV | 3 | 60 | 11440 | 25168 | Siemens
XXX-AAAAA-B2-MPM-02 | 4 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV | 3 | 60 | 11440 | 25168 | Siemens
XXX-AAAAA-B3-MPM-03 | 4 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV | 3 | 60 | 11440 | 25168 | Siemens
XXX-AAAAA-B4-MPM-04 | 4 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV | 3 | 60 | 11440 | 25168 | Siemens
MISC MOTORS - 460VAC | [10 empty] | All Sites
XXX-AAAAA-B0-PM-01 | 4 | Re-Injection Pump - 460VAC, 25 HP, 1.15 S.F, 1800RPM, TEFC, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | WEG Industrial SA
PUMP STATION - ELECTRIC ACTUATORS
MAINLINE PUMP ACTUATORS
XXX-AAAAA-B1-MOV-1011 | 4 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B1-MOV-1012 | 4 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B2-MOV-1021 | 4 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B2-MOV-1022 | 4 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B3-MOV-1031 | 4 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B3-MOV-1032 | 4 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B4-MOV-1041 | 4 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B4-MOV-1042 | 4 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
KXL-MV-SWGR | [10 empty] | All Sites
XXX-AAAAA-B0-SWGR-01 | 4 | 6.9kV SWGR | 2413 x 2591 x 2632 | 6.9kV | 3 | 60 | 3602 | 7924.4 | Siemens
XXX-AAAAA-B0-B-01 | 4 | 6.9kV Bus, 3000A |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-64-T-01 | 4 | Ground Fault Relay | [6 empty] | Startco
XXX-AAAAA-B0-52-B-01 | 4 | 6.9kV Breaker, 3000A (MAIN) |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-MFR-B-01 | 4 | Multi Function Relay | [6 empty] | Siemens
XXX-AAAAA-B0-MFR-PFCB-01 | 4 | Multi Function Relay | [6 empty] | Siemens
Breaker PFC UNIT
XXX-AAAAA-B0-52-PFCB-01 | 3 | 6.9kV Breaker, 1200A (POWER FACTOR CAPACITOR UNIT) |  | 6.9kV | 3 | 60 |  |  | Siemens |  | See designation table for sub area code and facility names
KXL-MV-MCC | [10 empty] | All Sites except for Leigh and Burns. Burns - 3 units only
XXX-AAAAA-B0-MCC-01 | 4 | 6.9kV MCC | 4648 x 1219 x 2608 | 6.9kV | 3 | 60 | 3515 | 7733 | Siemens
XXX-AAAAA-B0-B-01 | 4 | 6.9kV Bus, 3000A |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-89-VFD-01 | 4 | 6.9kV Contactor, 720A (VFD INPUT) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B0-MFR-VFD-01 | 4 | Multi Function Relay | [6 empty] | Siemens
XXX-AAAAA-B0-89-DT-01 | 4 | 6.9kV Contactor, 720A Station Service Transformer |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-MFR-DT-01 | 4 | Multi Function Relay | [6 empty] | Siemens
XXX-AAAAA-B1-89-01 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B1-MFR-MPM-01 | 4 | Motor Protection Relay | [6 empty] | Siemens
XXX-AAAAA-B2-89-01 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B2-MFR-MPM-02 | 4 | Motor Protection Relay | [6 empty] | Siemens
XXX-AAAAA-B3-89-01 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B3-MFR-MPM-03 | 4 | Motor Protection Relay | [6 empty] | Siemens
XXX-AAAAA-B4-89-01 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B4-MFR-MPM-04 | 4 | Motor Protection Relay | [6 empty] | Siemens
XXX-AAAAA-B5-89-01 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B5-MFR-MPM-05 | 4 | Motor Protection Relay | [6 empty] | Siemens
XXX-AAAAA-B0-MCC-02 | 4 | 6.9kV MCC | 3658 x 914 x 2286 | 6.9kV | 3 | 60 | 2812 | 6186.4 | Siemens
XXX-AAAAA-B0-B-02 | 4 | 6.9kV Bus, 1200A (VFD) |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-89-VFD-02 | 4 | 6.9kV Contactor, 720A (Isolation Output VFD) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B1-89-02 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B2-89-02 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B3-89-02 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B4-89-02 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B5-89-02 | 4 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  | 6.9kV | 3 | 60 |  |  | Toshiba
KXL-LV-MCC | [10 empty] | All Sites
XXX-AAAAA-B0-MCC-03 | 4 | 480V MCC | 2540 x 508 x 2286 * | 480V | 3 | 60 |  |  | Siemens |  | Size may vary in some stations.
XXX-AAAAA-B0-B-03 | 4 | 480V Bus, 800A |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-52-B-02 | 4 | 480V Breaker, 800A |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-MFR-B-02 | 4 | Multi Function Relay | [6 empty] | Siemens
XXX-AAAAA-B0-MCC-04 | 4 | 480V MCC (Emergency MCC) | 2540 x 508 x 610 | 480V | 3 | 60 |  |  | Siemens |  | Size may vary in some stations.
XXX-AAAAA-B0-B-04 | 4 | 480V Bus, 800A |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-ATS-01 | 4 | 480V Automatic transfer switch, 260A 3PH |  | 480V | 3 | 60 |  |  | ASCO
MISC KXL-EES-01 EQUIP'T | [10 empty] | All Sites
XXX-AAAAA-B0-DT-02 | 4 | Auxiliary Distribution Transformer 45kVA, 480-208/120V |  | 480- 208/120V | 3 | 60 |  |  | Hammond
XXX-AAAAA-B0-DT-03 | 4 | Auxiliary Distribution Transformer 45kVA, 480-208/120V |  | 480- 208/120V | 3 | 60 |  |  | Hammond
XXX-AAAAA-B0-UPS-01 | 4 | UPS, 7.5 kVA | 762 x 914 x 2007 | 208V | 3 | 60 | 422 | 928.4 | Ametek
XXX-AAAAA-B0-UACP-01 | 4 | 120V UPS Distribution Panel |  | 120VDC |  |  |  |  | Ametek
XXX-AAAAA-B0-BB-01 | 4 | UPS Battery Bank |  | 125VDC |  |  |  |  | East Pen
XXX-AAAAA-B0-ACP-01 | 4 | 208/120V Power Panel |  | 208/120V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-ACP-02 | 4 | 208/120V Power Panel |  | 208/120V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-EHTC-01 | 4 | EHT Control Panel | [6 empty] | Thermon |  | Not required for Gulf Coast Sites
XXX-AAAAA-B0-UCP-01 | 4 | Unit Control Panel | [6 empty] | Siemens
XXX-AAAAA-B0-SCP-01 | 4 | Station Control Panel | [6 empty] | GE
XXX-AAAAA-B0-HVAC-01 | 4 | Panel HVAC Unit 1, 6 Ton |  | 480V | 3 | 60 |  |  | Bard
XXX-AAAAA-B0-HVAC-02 | 4 | Panel HVAC Unit 2, 6 Ton |  | 480V | 3 | 60 |  |  | Bard
XXX-AAAAA-B0-HVAC-03 | 4 | Panel HVAC Unit 3, 6 Ton |  | 480V | 3 | 60 |  |  | Bard
XXX-AAAAA-B0-SCMP-01 | 4 | Station Communication Panel
XXX-AAAAA-B0-CR-01 | 4 | Cathodic Protection Rectifier | [6 empty] | Corrpro |  | Site specific - if required
XXX-AAAAA-B0-SCMP-03 | 4 | Service Entrance Box | [6 empty] | Siemens
XXX-AAAAA-B0-CP-01 | 4 | Mimic Panel | [6 empty] | Koontz Wagner
Rexa Panel/ Transformer
XXX-AAAAA-B0-PFCB-01 | 3 | Power Factor Capacitor Bank |  | 6.9kV | 3 | 60 |  |  | Power Survey
STATION ACTUATORS
Sites with 3-valve cluster
XXX-AAAAA-B0-MOV-0101 | 2 | Suction - 460VAC, 1.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0205 | 2 | Disch. - 460VAC, 1.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0102 | 2 | Bypass - 460VAC, 1.5 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
Sites with trap
XXX-AAAAA-B0-MOV-0101 | 2 | Suction - 460VAC, 0.25 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0205 | 2 | Discharge - 460VAC, 0.25 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0102 | 2 | Bypass - 460VAC, 6.0 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
PIG TRAP ACTUATORS
XXX-AAAAA-B0-MOV-0103 | 2 | Receiver - 460VAC, 25 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0104 | 2 | Receiver - 460VAC, 25 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0107 | 2 | Receiver - 460VAC, 30 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0203 | 2 | Launcher - 460VAC, 25 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0204 | 2 | Launcher - 460VAC, 25 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0207 | 2 | Launcher - 460VAC, 30 HP, CL 1, DIV.1 GR D |  | 460V | 3 | 60 |  |  | EIM
EHT CONTROLLER FOR SUMP TANK
XXX-AAAAA-B0-EHTC-03 | 4 | EHT Control Panel, Part No. TCM2-1-SSR30B/1R-240-I-1SS3-H1-1-1-178525 | [6 empty] | Thermon

## Sheet1
TAG NUMBER | QTY OF ITEMS | DESCRIPTION | SIZE |  | VOLTS | PHASE | FREQUENCY | SHIPPING WEIGHT | SHIPPING DIMENSIONS | MFR | MODEL | SUPPLIED BY (COMPANY, CONTRACTOR, FABRICATOR) | PO AND PO LINE NO. (IF COMPANY SUPPLY) | COMMENTS | REV
[7 empty] | Hz | kg | m
KXL-EES-01 | [13 empty] | All Sites
XXX-AAAAA-B0-EES-01 | 1 | Electrical Equipment Shelter - Premanufactured Steel building | 18593 x 4267 x 3962 |  |  |  |  | 38555 |  | Koontz Wagner
KXL-VES-01 | [13 empty] | All Sites
XXX-AAAAA-B0-VES-01 | 1 | VFD Equipment Shelter - Premanufactured Steel building | 10668 x 4267 x 4318 |  |  |  |  | 39689 |  | Koontz Wagner
KXL-MV-VFD
XXX-AAAAA-B0-VFD-01 | 1 | MV 6500hp VFD | 7823 x 1372 x 3256 |  | 6.9kV | 3 | 60 | - |  | Siemens
XXX-AAAAA-B0-LBS-01 | 1 | MV VFD Incomer Load Break Switch | 914 x 1118 x 2362 |  | 6.9kV | 3 | 60 | - |  | Siemens
XXX-AAAAA-B0-ACP-03 | 1 | 480V Auxiliary Distribution Panel |  |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-LDP-01 | 1 | Lighting Distribution Panel |  |  | 120/ 240V | 1 | 60 |  |  | Siemens
XXX-AAAAA-B0-TL-01 | 1 | Lighting Distribution Transformer |  |  | 480- 240/120V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-HVAC-04 | 1 | Panel HVAC Unit 4, 30 Ton |  |  | 480V | 3 | 60 |  |  | Specific Systems
XXX-AAAAA-B0-HVAC-05 | 1 | Panel HVAC Unit 5, 30 Ton |  |  | 480V | 3 | 60 |  |  | Specific Systems
XXX-AAAAA-B0-HVAC-06 | 1 | Panel HVAC Unit 6, 30 Ton |  |  | 480V | 3 | 60 |  |  | Specific Systems
XXX-AAAAA-B0-EJB-1011 | 1 | Control Interface Panel
PUMP STATION - ELECTRIC EQUIPMENT OUTDOOR | [13 empty] | All Sites
XXX-AAAAA-B0-DT-01 | 1 | Station Service Transformer 600kVA, 6900-480V | 2753 x 1878 x 1907 | 6900-480V |  | 3 | 60 | 3719 |  | Virginia Transformer
XXX-AAAAA-B0-EG-01 | 1 | Emergency Genarator | 4826 x 1013 x 3070 | 480V |  | 3 | 60 | 3960 |  | Generac
XXX-AAAAA-B0-GCP-01 | 1 | Emergency Genarator control panel |  | 208V |  | 3 | 60 |  |  | Generac
PUMP STATION - ELECTRIC MOTORS
MAINLINE PUMP MOTORS - 6.6kV
XXX-AAAAA-B1-MPM-01 | 1 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV |  | 3 | 60 | 11440 |  | Siemens
XXX-AAAAA-B2-MPM-02 | 1 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV |  | 3 | 60 | 11440 |  | Siemens
XXX-AAAAA-B3-MPM-03 | 1 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV |  | 3 | 60 | 11440 |  | Siemens
XXX-AAAAA-B4-MPM-04 | 1 | 6.6kV, 6500 HP, 1.15 S.F, 1800 RPM, WP2, CL 1, DIV.2 GR D | 2972 x 3068 x 1946 | 6.6kV |  | 3 | 60 | 11440 |  | Siemens
MISC MOTORS - 460VAC | [13 empty] | All Sites
XXX-AAAAA-B0-PM-01 | 1 | Re-Injection Pump - 460VAC, 25 HP, 1.15 S.F, 1800RPM, TEFC, CL 1, DIV.1 GR D |  | 460V |  | 3 | 60 |  |  | WEG Industrial SA
PUMP STATION - ELECTRIC ACTUATORS
MAINLINE PUMP ACTUATORS
XXX-AAAAA-B1-MOV-1011 | 1 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B1-MOV-1012 | 1 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM |  |  |  |  | 2
XXX-AAAAA-B2-MOV-1021 | 1 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B2-MOV-1022 | 1 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM |  |  |  |  | 2
XXX-AAAAA-B3-MOV-1031 | 1 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B3-MOV-1032 | 1 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM |  |  |  |  | 2
XXX-AAAAA-B4-MOV-1041 | 1 | Suction - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B4-MOV-1042 | 1 | Discharge - 460VAC, 0.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM |  |  |  |  | 2
KXL-MV-SWGR | [13 empty] | All Sites
XXX-AAAAA-B0-SWGR-01 | 1 | 6.9kV SWGR | 2413 x 2591 x 2632 |  | 6.9kV | 3 | 60 | 3602 |  | Siemens
XXX-AAAAA-B0-B-01 | 1 | 6.9kV Bus, 3000A |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-64-T-01 | 1 | Ground Fault Relay | [7 empty] | Startco
XXX-AAAAA-B0-52-B-01 | 1 | 6.9kV Breaker, 3000A (MAIN) |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-MFR-B-01 | 1 | Multi Function Relay | [7 empty] | Siemens
XXX-AAAAA-B0-MFR-PFCB-01 | 1 | Multi Function Relay | [7 empty] | Siemens
Breaker PFC UNIT
XXX-AAAAA-B0-52-PFCB-01 | 1 | 6.9kV Breaker, 1200A (POWER FACTOR CAPACITOR UNIT) |  |  | 6.9kV | 3 | 60 |  |  | Siemens |  |  |  | See designation table for sub area code and facility names
KXL-MV-MCC | [13 empty] | All Sites except for Leigh and Burns. Burns - 3 units only
XXX-AAAAA-B0-MCC-01 | 1 | 6.9kV MCC | 4648 x 1219 x 2608 |  | 6.9kV | 3 | 60 | 3515 |  | Siemens
XXX-AAAAA-B0-B-01 | 1 | 6.9kV Bus, 3000A |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-89-VFD-01 | 1 | 6.9kV Contactor, 720A (VFD INPUT) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B0-MFR-VFD-01 | 1 | Multi Function Relay | [7 empty] | Siemens
XXX-AAAAA-B0-89-DT-01 | 1 | 6.9kV Contactor, 720A Station Service Transformer |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-MFR-DT-01 | 1 | Multi Function Relay | [7 empty] | Siemens
XXX-AAAAA-B1-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B1-MFR-MPM-01 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B2-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B2-MFR-MPM-02 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B3-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B3-MFR-MPM-03 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B4-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B4-MFR-MPM-04 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B5-89-01 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Bypass) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B5-MFR-MPM-05 | 1 | Motor Protection Relay | [7 empty] | Siemens
XXX-AAAAA-B0-MCC-02 | 1 | 6.9kV MCC | 3658 x 914 x 2286 |  | 6.9kV | 3 | 60 | 2812 |  | Siemens
XXX-AAAAA-B0-B-02 | 1 | 6.9kV Bus, 1200A (VFD) |  |  | 6.9kV | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-89-VFD-02 | 1 | 6.9kV Contactor, 720A (Isolation Output VFD) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B1-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B2-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B3-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B4-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
XXX-AAAAA-B5-89-02 | 1 | 6.9kV Contactor, 720A, 6500hp (VFD Output) |  |  | 6.9kV | 3 | 60 |  |  | Toshiba
KXL-LV-MCC | [13 empty] | All Sites
XXX-AAAAA-B0-MCC-03 | 1 | 480V MCC | 2540 x 508 x 2286 * |  | 480V | 3 | 60 |  |  | Siemens |  |  |  | Size may vary in some stations.
XXX-AAAAA-B0-B-03 | 1 | 480V Bus, 800A |  |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-52-B-02 | 1 | 480V Breaker, 800A |  |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-MFR-B-02 | 1 | Multi Function Relay | [7 empty] | Siemens
XXX-AAAAA-B0-MCC-04 | 1 | 480V MCC (Emergency MCC) | 2540 x 508 x 610 |  | 480V | 3 | 60 |  |  | Siemens |  |  |  | Size may vary in some stations.
XXX-AAAAA-B0-B-04 | 1 | 480V Bus, 800A |  |  | 480V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-ATS-01 | 1 | 480V Automatic transfer switch, 260A 3PH |  |  | 480V | 3 | 60 |  |  | ASCO
MISC KXL-EES-01 EQUIP'T | [13 empty] | All Sites
XXX-AAAAA-B0-DT-02 | 1 | Auxiliary Distribution Transformer 45kVA, 480-208/120V |  |  | 480- 208/120V | 3 | 60 |  |  | Hammond
XXX-AAAAA-B0-DT-03 | 1 | Auxiliary Distribution Transformer 45kVA, 480-208/120V |  |  | 480- 208/120V | 3 | 60 |  |  | Hammond
XXX-AAAAA-B0-UPS-01 | 1 | UPS, 7.5 kVA | 762 x 914 x 2007 |  | 208V | 3 | 60 | 422 |  | Ametek
XXX-AAAAA-B0-UACP-01 | 1 | 120V UPS Distribution Panel |  |  | 120VDC |  |  |  |  | Ametek
XXX-AAAAA-B0-BB-01 | 1 | UPS Battery Bank |  |  | 125VDC |  |  |  |  | East Pen
XXX-AAAAA-B0-ACP-01 | 1 | 208/120V Power Panel |  |  | 208/120V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-ACP-02 | 1 | 208/120V Power Panel |  |  | 208/120V | 3 | 60 |  |  | Siemens
XXX-AAAAA-B0-EHTC-01 | 1 | EHT Control Panel | [7 empty] | Thermon |  |  |  | Not required for Gulf Coast Sites
XXX-AAAAA-B0-UCP-01 | 1 | Unit Control Panel | [7 empty] | Siemens
XXX-AAAAA-B0-SCP-01 | 1 | Station Control Panel | [7 empty] | GE
XXX-AAAAA-B0-HVAC-01 | 1 | Panel HVAC Unit 1, 6 Ton |  |  | 480V | 3 | 60 |  |  | Bard
XXX-AAAAA-B0-HVAC-02 | 1 | Panel HVAC Unit 2, 6 Ton |  |  | 480V | 3 | 60 |  |  | Bard
XXX-AAAAA-B0-HVAC-03 | 1 | Panel HVAC Unit 3, 6 Ton |  |  | 480V | 3 | 60 |  |  | Bard
XXX-AAAAA-B0-SCMP-01 | 1 | Station Communication Panel
XXX-AAAAA-B0-CR-01 | 1 | Cathodic Protection Rectifier | [7 empty] | Corrpro |  |  |  | Site specific - if required
XXX-AAAAA-B0-SCMP-03 | 1 | Service Entrance Box | [7 empty] | Siemens
XXX-AAAAA-B0-CP-01 | 1 | Mimic Panel | [7 empty] | Koontz Wagner
Rexa Panel/ Transformer
XXX-AAAAA-B0-PFCB-01 | 1 | Power Factor Capacitor Bank |  |  | 6.9kV | 3 | 60 |  |  | Power Survey
STATION ACTUATORS
Sites with 3-valve cluster
XXX-AAAAA-B0-MOV-0101 | 1 | Suction - 460VAC, 1.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0205 | 1 | Disch. - 460VAC, 1.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0102 | 1 | Bypass - 460VAC, 1.5 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
Sites with trap
XXX-AAAAA-B0-MOV-0101 | 1 | Suction - 460VAC, 0.25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0205 | 1 | Discharge - 460VAC, 0.25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0102 | 1 | Bypass - 460VAC, 6.0 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
PIG TRAP ACTUATORS
XXX-AAAAA-B0-MOV-0103 | 1 | Receiver - 460VAC, 25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0104 | 1 | Receiver - 460VAC, 25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0107 | 1 | Receiver - 460VAC, 30 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0203 | 1 | Launcher - 460VAC, 25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0204 | 1 | Launcher - 460VAC, 25 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
XXX-AAAAA-B0-MOV-0207 | 1 | Launcher - 460VAC, 30 HP, CL 1, DIV.1 GR D |  |  | 460V | 3 | 60 |  |  | EIM
EHT CONTROLLER FOR SUMP TANK
XXX-AAAAA-B0-EHTC-03 | 1 | EHT Control Panel, Part No. TCM2-1-SSR30B/1R-240-I-1SS3-H1-1-1-178525 | [7 empty] | Thermon |  | CONTRACTOR |  |  | 2